# DEVELOPMENT SERVICES

Building Standards Division

349 North Center St.  PO Box 788			Phone: 704-928-2021

Statesville, NC 28687					Fax: 704-878-3122

Mr. Jeremy L Roh								Daniel Poole: x3119

Ragona Architecture and Design						dpoole@co.iredell.nc.us

#### RE:	Fairfield Inn and Suites – Permit #247386 			September 17, 2019

###### Statesville

Dear Mr. Roh:

Plans relative to the above named project have been reviewed for general compliance with the North Carolina State Building Code with the following comments:

- Need to verify the use of moisture resistant gypsum board or other substrate on the first floor gang restroom walls.

- Need to show the locations of all overflow drainage outlets on the elevations.

- Porte cochere overflow drainage must be piped to a conspicuous and readily visible outlet. Provide plans and details showing this required piping and outlet.

- On sheet A.801, gates P1 and P2 must have panic hardware attached.

- On sheet A.801, door 148A must have panic hardware attached.

- At detail 3 on sheet A.803, the upper side lite window beside the door must have tempered glazing.

- Need a valid exit discharge past exterior egress door 110.  Need to provide a minimum 4 foot wide concrete sidewalk between door 110 and door 148B. Revise all civil drawings.

- On the civil utility plans, need to show separate sanitary drainage lines and grease waste drainage lines exiting building.  Plan only shows one line exiting the building and entering the grease trap.  Only grease line waste may enter trap – all other waste must bypass trap.

- On sheet E.301, fire alarm system visual indicating devices (strobes) were left out of the bathroom on details 1, 2, 4, and 6.

- Re-submit 2 copies of each revised sheet along with a written response indicating all changes or additions.

- Need soil bearing report.  Maximum allowed assumed bearing pressure in Iredell County is 2,000 pounds.  Report must be submitted before permits can be issued.

- Need City of Statesville Zoning Department letter of approval and/or permission to issue permits and start construction.  These restrictions must be removed from the computer system before permits can be generated.

- A copy of the Plan Review Approval letter from the Iredell County Health Department’s Environmental Health Division must be submitted for this project. You may contact Ms. Kim Mecimore of the Environmental Health Division by calling 704-902-4485 or email her at kmecimore@co.iredell.nc.us.

Page 2

Mr. Jeremy L Roh

September 17, 2019

- A copy of the Plan Review Approval letter from the City of Statesville’s Water Resources Department must be submitted for the Grease Interceptor in this project. You may contact Ms. Brandy Johnson in the Pretreatment Office by calling 704-878-3438 or email her at bjohnson@statesvillenc.net.

- A copy of the Plan Review Approval letter from the City of Statesville’s Fire Marshal’s Office must be submitted for this project. You may contact Mr. Maury Jenkins in the Fire Marshal’s Office by calling 704-832-3877 or email him at mjenkins@statesvillenc.net.

We will await further information from you concerning this project.

Best Regards,

Daniel W. Poole

Plans Examiner

The contents of this communication indicate the required items which need to be addressed prior to issuance of the permits for the project. This information will be provided to the designated contact person for the project and the lead design professional as listed on the plan review application and/or plans as well as other authorities having jurisdiction.  The issuance of a permit or approval of plans or specifications shall not be deemed or construed to be approval of any violation of any of the provisions of the North Carolina State Building Codes, or State, or local ordinances or regulations.