# DEVELOPMENT SERVICES

Building Standards Division

349 North Center St.  PO Box 788			Phone: 704-928-2021

Statesville, NC 28687					Fax: 704-878-3122

Mr. Jeremy L Roh								Daniel Poole: x3119

Ragona Architecture and Design						dpoole@co.iredell.nc.us

#### RE:	Fairfield Inn and Suites – Permit #247386 			October 9, 2019

###### Statesville

Dear Mr. Roh:

Plans relative to the above named project have been reviewed for general compliance with the North Carolina State Building Code with the following comments:

- September 17, 2019 comment: Porte cochere overflow drainage must be piped to a conspicuous and readily visible outlet. Provide plans and details showing this required piping and outlet. October 9, 2019 comment: On sheet A303, at detail 6 “hidden elevation F”, show overflow outlet. See newly revised sheet P100.  Re-submit two copies of sheet A303.

- September 17, 2019 comment: On sheet E.301, fire alarm system visual indicating devices (strobes) were left out of the bathroom on details 1, 2, 4, and 6. October 9, 2019 comment: On sheet E.301, strobes are already shown in the sleeping room but are not shown in the bathroom at each of the four details.  For consistency with all other details on this sheet and all details on sheet E302, show the strobes in the bathroom and link them to the “cf room…” note. Otherwise, coordinate with architectural drawings and show strobes on only the room details that require them.  Re-submit two copies of sheet E.301 (and E.302 if necessary).

- Need City of Statesville Zoning Department letter of approval and/or permission to issue permits and start construction.  These restrictions must be removed from the computer system before permits can be generated.  Project currently has “PLANS REVIEW ONLY” status.

- A copy of the Plan Review Approval letter from the Iredell County Health Department’s Environmental Health Division must be submitted for this project. You may contact Ms. Kim Mecimore of the Environmental Health Division by calling 704-902-4485 or email her at kmecimore@co.iredell.nc.us.

- A copy of the Plan Review Approval letter from the City of Statesville’s Fire Marshal’s Office must be submitted for this project. You may contact Mr. Maury Jenkins in the Fire Marshal’s Office by calling 704-832-3877 or email him at mjenkins@statesvillenc.net.

We will await further information from you concerning this project.

Best Regards,

Daniel W. Poole

Plans Examiner

The contents of this communication indicate the required items which need to be addressed prior to issuance of the permits for the project. This information will be provided to the designated contact person for the project and the lead design professional as listed on the plan review application and/or plans as well as other authorities having jurisdiction.  The issuance of a permit or approval of plans or specifications shall not be deemed or construed to be approval of any violation of any of the provisions of the North Carolina State Building Codes, or State, or local ordinances or regulations.