# DEVELOPMENT SERVICES

Building Standards Division

349 North Center St.  PO Box 788			Phone: 704-928-2021

Statesville, NC 28687					Fax: 704-878-3122

Ms. Amy Williams								Daniel Poole: x3119

Housing Studio								dpoole@co.iredell.nc.us

#### RE:	Mill One Apartments/Retail – Permit #306336			April 15, 2020

###### Mooresville

Dear Ms. Williams:

Plans relative to the above named project have been reviewed for general compliance with the North Carolina State Building Code with the following comments:

- All civil drawings must be sealed, signed, and dated by designer of record.

- Will need accessible passenger loading zone at designated loading zone.

- Parallel accessible parking spaces must have access aisles adjacent to each space.

- Curbs appear to surround building with no indication of wheelchair access.  At all accessible parking access aisles front and back of building and at any other location in need of access such as the loading zone, need to provide accessible curb ramps.

- Need accessible route from building to dumpster and recycling area.

- Need plans, details, and sections for all stairs, handrails, and guards on site.

- On the building code summary on sheet A0.04, fill in special provisions section.

- At all floor plans and sections throughout, label exterior walls with wall type used.

- On sheet A0.04, provide a table to describe how lower floor construction is 3-hour rated.  Explain how floor slab and all supporting construction is 3-hour protected using the provisions of chapter 7 of the 2018 North Carolina Building Code.  Specify table number, page number, and section number of all calculated fire resistance elements used.

- On sheet A0.04, fill in the fire protection requirements table correctly for bearing walls and floor construction.

- On sheet A0.04, in the fire protection requirements table, floor construction is required to be 3-hour rated.

- On sheet A0.06, need to wrap corridor walls around mechanical closets.  Not including closet within the envelope of the corridor will require multiple fire/smoke dampers at each closet.

- On sheet A0.20 at details 22C and 22B, the cast in place concrete wall must be rated at 3 hours minimum.

- On sheet A4.01A, label door 101E.

- On sheet A4.01B, label doors 121A, 121B, and 128B.

Page 2

Ms. Amy Williams

April 15, 2020

- On sheet A4.01B, coordinate with electrical – doors 124B and 139A cannot be blocked by electrical gear inside each room.

- Need panic hardware on the following doors: 119A, 124A, 124B, 139A, 139B, 213A, 218A, 313A, 318A, 413A, and 418A.  Electrical gear beyond each of these doors is 800 amps or more.

- On sheet A4.04A, label door 403A.

- On sheet S1.0.0, snow load for Iredell County is 15 pounds per square foot.

- For all electrical drawings for all individual apartment units, smoke detectors are required in each sleeping room and outside each sleeping area.  Revise all electrical plans.

- On sheet E4.1B, need regular electrical lighting outside doors 136A and 137A.

- On apartment unit mechanical plans, show what methods are used to exceed maximum length of 35 feet for dryer exhaust ductwork in all applicable units.  Reference 2018 North Carolina Mechanical Code section 504.8.

- Need complete post tension slab plans and details.  Plans must be sealed, signed, and dated throughout by designer of record.

- Re-submit 1 complete bound set of revised drawings along with a written response indicating all changes or additions.

- Need Town of Mooresville Zoning Department letter of approval and/or permission to issue permits and start construction.  These restrictions must be removed from the computer system before permits can be generated.

- Need Town of Mooresville Wastewater Department letter of approval and/or permission to install grease interceptors.

- Need Town of Mooresville Fire Marshal letter of approval and/or permission to issue permits and start construction.

We will await further information from you concerning this project.

Best Regards,

Daniel W. Poole

Plans Examiner

The contents of this communication indicate the required items which need to be addressed prior to issuance of the permits for the project. This information will be provided to the designated contact person for the project and the lead design professional as listed on the plan review application and/or plans as well as other authorities having jurisdiction.  The issuance of a permit or approval of plans or specifications shall not be deemed or construed to be approval of any violation of any of the provisions of the North Carolina State Building Codes, or State, or local ordinances or regulations.